# INTERNAL AUDIT REPORT

Fire Hazard & Life Safety Controls – Branch Audit
ABC Bank

# Table of Contents

1. Executive Summary

2. Audit Objectives

3. Scope of Audit

4. Methodology

5. Rating Matrix

6. Detailed Observations

7. Management Action Plan

8. Conclusion

9. Approvals

# 1. Executive Summary

The Internal Audit function conducted a Fire Hazard & Life Safety review of ABC Bank – XYZ Branch. Ten observations were identified, including significant risks in fire equipment readiness, evacuation preparedness, electrical safety, and documentation gaps. The overall risk rating is HIGH.

# 2. Audit Objectives

- Assess fire safety control effectiveness
- Verify compliance with regulatory and internal safety requirements
- Evaluate emergency response preparedness
- Review documentation, housekeeping, and training practices

# 3. Scope of Audit

Reviewed period: Jan 2025 – Oct 2025
On-site review: Nov 22–23, 2025
Areas covered: fire extinguishers, alarms, detectors, electrical safety, server room, evacuation paths, training logs.

# 4. Methodology

• Walkthroughs • Evidence sampling • Staff interviews • Documentation review • Regulatory alignment checks

# 5. Rating Matrix

High – Severe risk, immediate remediation required
Medium – Moderate risk, remediation required
Low – Minor deviation, improvement recommended

# 6. Detailed Audit Observations

## Observation 1: Fire Extinguishers Not Serviced or Expired

Risk Rating: High

6 of 14 extinguishers expired; low pressure detected; vendor contract lapsed.

## Observation 2: Emergency Exits Blocked

Risk Rating: High

Exit path obstructed with cartons; no signage displayed.

## Observation 3: Smoke Detectors Non-functional in Server Room

Risk Rating: High

Two detectors failed test; Fire Panel showed fault but not escalated.

## Observation 4: No Evacuation Drill in Last 12 Months

Risk Rating: High

Last drill in July 2024; regulation mandates biannual drills.

## Observation 5: Exposed Electrical Wiring

Risk Rating: Medium

Live wiring exposed under Teller Counter 3; conduit damaged.

## Observation 6: Fire Alarm Panel Missing Zone Labels

Risk Rating: Medium

Zones unlabeled, delaying fire source identification.

## Observation 7: Insufficient Fire Safety Signage

Risk Rating: Medium

Missing assembly point and exit direction signs.

## Observation 8: Combustible Items Near Electrical Panels

Risk Rating: Medium

Paper and cleaning stock stored near DB board.

## Observation 9: Staff Fire Training Incomplete

Risk Rating: Low

Only 2 of 18 employees trained in extinguisher usage.

## Observation 10: FM200 Logs Missing

Risk Rating: Low

3 months of fire suppression logs missing; vendor not documenting.

# 7. Management Action Plan Summary

| Observation | Risk | Target Closure Date | Owner |
| --- | --- | --- | --- |
| Observation 1: Fire Extinguishers Not Serviced or Expired | High | Jan 15 2026 | Branch Ops Manager |
| Observation 2: Emergency Exits Blocked | High | Immediate | Branch Manager |
| Observation 3: Smoke Detectors Non-functional in Server Room | High | Dec 20 2025 | IT Custodian |
| Observation 4: No Evacuation Drill in Last 12 Months | High | Jan 10 2026 | Safety Officer |
| Observation 5: Exposed Electrical Wiring | Medium | 30–60 days | Dept Owner |
| Observation 6: Fire Alarm Panel Missing Zone Labels | Medium | 30–60 days | Dept Owner |
| Observation 7: Insufficient Fire Safety Signage | Medium | 30–60 days | Dept Owner |
| Observation 8: Combustible Items Near Electrical Panels | Medium | 30–60 days | Dept Owner |
| Observation 9: Staff Fire Training Incomplete | Low | 30–60 days | Dept Owner |
| Observation 10: FM200 Logs Missing | Low | 30–60 days | Dept Owner |

# 8. Conclusion

The branch has significant fire hazard risks requiring urgent remediation. A follow-up audit is recommended within 90 days.

# 9. Approvals

Prepared By: Internal Audit – Safety & Compliance Division

Reviewed By: Chief Internal Auditor

Approved By: Head of Internal Audit